## Data (1)
ITRC Pump Efficiency Test Report | [7 empty] | Do not edit
2004-03-12
Nameplate HP on motor: |  | 50 | Flow Measurement Work Area |  |  |  |  | Collins or Prandtl Tube
Motor RPM |  | 1770 | Choose Flow Rate Test Method |  |  |  |  | Hall Tube
Motor Efficiency |  | 85% | Pipe OD (inches) |  |  | 6.8 |  | Other type of flow meter
Meter factor (Kh): |  | 28.8 | Pipe wall thickness (inches) |  |  | 0.119 |  |  | 1
Power Factor |  | 0.95 | Pipe ID (inches) |  |  | 6.681 |  | Check | 519.6299
Depth of Pump |  |  | Find the box below that represents your flow test method. Look for "Complete"
Pump Make |  |  | Collins or Prandtl tube measurement |  |  |  | Complete
Driver Make |  |  | If you have no data, leave or make blank do not enter 0
Discharge Head Type |  |  | Velocity Measurement (ft/s) - single transect
Column Diameter (in) |  | 7 | Left of CL | 4.9 | 5.1 | 5.3
Shaft Length (ft) |  |  | Right of CL | 4.7 | 4.8 | 4.3
Shaft Diameter (inches) |  |  | Avg. transect velocity (ft/s) |  |  | 4.85
Vertical Pump TDH Data |  |  | Velocity Measurement (ft/sec) - second transect for Collins Tube
Standing Water Level below ground (ft) |  |  | Left of CL
Drawdown (ft) | 1 | Need PWL | Right of CL
Pumping Water Level (ft) |  |  | Average transect velocity (ft/s)
Column and screen Friction Losses (ft)
Discharge Head Loss (ft) |  |  | GPM Calculation
|  |  | Avg. velocity in the pipe (ft/s) |  |  | 4.85
Horizontal Pump TDH Data |  |  | Conversion for manometers |  |  | 0 | if applicable
Suction pressure (inches Hg) |  | -21.2 | Revised average velocity |  |  | 4.85
Suction pressure (ft) | 1a | -24.0196 | Pipe ID |  |  | 6.681
Suction pressure gauge height above ground (ft) |  | 5 | Multiplier |  |  | 107.1402
|  |  | Calculated GPM |  |  | 519.6299
Discharge pressure data for all pumps |  |  | OR
Discharge pipe centerline above ground (ft) |  | 3 | Hall tube measurement |  |  |  | Ignore
Height of gauge above ground (ft) |  | 3 | Avg. Velocity of a single transect (ft/s)
Discharge pressure at gauge (psi) |  | 85 | Avg. Velocity of second transect (ft/s)
Discharge pressure at gauge (ft) | 2 | 193.35 | Calculated GPM |  |  | 0
Total lift (ft) (commonly used by pump testers) | 3 | 29.0196
Total dynamic head (ft) | 4 | 218.3696 | OR
Flow rate (GPM) |  | 519.6299 |  |  |  |  | Ignore
Water horsepower | 5 | 28.6544 | Other type of flow meter (GPM)
Water kW |  | 21.3762
KW Calculation (Choose a method)
1. Number of dial rotations |  | 5 | Only needed if option 3 is chosen, otherwise ignore |  |  |  |  | 1.Dial Rotation | 1
Time for dial rotations (secs) |  | 14.1 | 3. Alternate volt-amp method for KW |  |  |  | Ignore | 2.Portable Meter | 2
Meter Constant |  | 1 | KW = V x A x PF x 1.732 / 1000 |  |  |  |  | 3.Volt-Amp Method | 3
Meter Factor, Kh |  | 28.8 | Do not input 0 - Leave blank for no data
KW from Meter |  | 36.7984 |  | 1 | 2 | 3 | avg | Answer | 1
OR |  |  | Volts |  |  |  |  | Check | 36.7984
2. KW from portable meter |  |  | Amps
OR | [5 empty] | Power Factor | 0.95
3. KW from volt-amp method (Use table at right) |  | Ignored |  |  |  | KW | 0
Answer - KW Calculation | 36.7984
Input Horsepower | 6 | 49.3277 |  |  | Motor Load
Estimated thrust bearing losses (hp) | 6a | 0.41929 |  |  | Motor Eff. | 85% | C5
Estimated shaft losses (hp) | 6b | Need Shaft Length |  |  | Nameplate HP | 50 | C3
Brake horsepower delivered to impeller (hp) | 7 | 41.5092 |  |  | Nplt Input HP | 58.8235
Impeller Efficiency (%) | 8 | 69.03% |  |  | Input HP | 49.3277
Overall Pumping Plant Efficiency (%) | 9 | 58.09% |  |  | Motor Load | 83.86%
KWH/AF | 10 | 384.5933
1 Pumping water level = Standing water level + Drawdown, 1a. Suction inches Hg = 1.133 ft of water
2 Discharge pressure at gauge (feet) = (Discharge pressure at gauge (psi) x 2.31 ) - Height of gauge above ground (ft)
3 Total lift = Pumping water level + Discharge pipe centerline above ground + Discharge pressure (all in feet)
OR (Horizontal Pumps) Total lift = Suction pressure (ft) - Suction pressure gauge height above ground (ft)
4 Total dynamic head (ft) =Total lift + Column friction losses + Discharge head loss
5 Water Horsepower = GPM x Total Dynamic Head/3960
6 Input HP =4.83 x (Kh for meter) x (M, usually = 1) x (Number of Meter Revolutions) / (Time for meter rev. in sec)
OR Input Horsepower =(KW from test meter) / 0.746
OR Input Horsepower =(KW from volt-amp method / 0.746)
6a Est. thrust bearing losses = Motor Eff*Input HP*1%
6b Est. shaft losses = 1HP per 100 feet of shaft (Shaft length in cell C13 is needed for this calc otherwise it is ignored)
7 Brake Horsepower delivered to impeller = (Input Horsepower * Motor Efficiency) - Est. thrust bearing losses - Est. shaft losses
(If no shaft length input in C10 shaft loss is ignored)
8 Impeller Efficiency (%) = Water Horsepower / Brakehorsepower x 100
9 Overall Pumping Plant Efficiency (%) = Water Horsepower/Input Horsepower x 100
10 KWH/AF = (IHP * .746)/ (GPM *60/325,850)

## Data (2)
ITRC Pump Efficiency Test Report | [7 empty] | Do not edit
2004-03-12
Nameplate HP on motor: |  | 20 | Flow Measurement Work Area |  |  |  |  | Collins or Prandtl Tube
Motor RPM |  | 1770 | Choose Flow Rate Test Method |  |  |  |  | Hall Tube
Motor Efficiency |  | 85% | Pipe OD (inches) |  |  | 12.3 |  | Other type of flow meter
Meter factor (Kh): |  | 28.8 | Pipe wall thickness (inches) |  |  | 0.119 |  |  | 3
Power Factor |  | 0.95 | Pipe ID (inches) |  |  | 12.181 |  | Check | 1400
Depth of Pump |  |  | Find the box below that represents your flow test method. Look for "Complete"
Pump Make |  |  | Collins or Prandtl tube measurement |  |  |  | Ignore
Driver Make |  |  | If you have no data, leave or make blank do not enter 0
Discharge Head Type |  |  | Velocity Measurement (ft/s) - single transect
Column Diameter (in) |  | 12 | Left of CL
Shaft Length (ft) |  | 9 | Right of CL
Shaft Diameter (inches) |  |  | Avg. transect velocity (ft/s)
Vertical Pump TDH Data |  |  | Velocity Measurement (ft/sec) - second transect for Collins Tube
Standing Water Level below ground (ft) |  | 9 | Left of CL
Drawdown (ft) | 1 | 0 | Right of CL
Pumping Water Level (ft) |  | 9 | Average transect velocity (ft/s)
Column and screen Friction Losses (ft) |  | 1
Discharge Head Loss (ft) |  |  | GPM Calculation
Avg. velocity in the pipe (ft/s)
Horizontal Pump TDH Data |  |  | Conversion for manometers |  |  | 0 | if applicable
Suction pressure (inches Hg) |  |  | Revised average velocity
Suction pressure (ft) | 1a | 0 | Pipe ID |  |  | 12.181
Suction pressure gauge height above ground (ft) |  |  | Multiplier |  |  | 363.5231
|  |  | Calculated GPM |  |  | 0
Discharge pressure data for all pumps |  |  | OR
Discharge pipe centerline above ground (ft) |  | 5 | Hall tube measurement |  |  |  | Ignore
Height of gauge above ground (ft) |  |  | Avg. Velocity of a single transect (ft/s)
Discharge pressure at gauge (psi) |  | 15 | Avg. Velocity of second transect (ft/s)
Discharge pressure at gauge (ft) | 2 | 34.65 | Calculated GPM |  |  | 0
Total lift (ft) (commonly used by pump testers) | 3 | 48.65
Total dynamic head (ft) | 4 | 49.65 | OR
Flow rate (GPM) |  | 1400 |  |  |  |  | Complete
Water horsepower | 5 | 17.553 | Other type of flow meter (GPM) |  |  | 1400
Water kW |  | 13.0946
KW Calculation (Choose a method)
1. Number of dial rotations |  |  | Only needed if option 3 is chosen, otherwise ignore |  |  |  |  | 1.Dial Rotation | 1
Time for dial rotations (secs) |  |  | 3. Alternate volt-amp method for KW |  |  |  | Ignore | 2.Portable Meter | 2
Meter Constant |  |  | KW = V x A x PF x 1.732 / 1000 |  |  |  |  | 3.Volt-Amp Method | 3
Meter Factor, Kh |  |  | Do not input 0 - Leave blank for no data
KW from Meter |  | Ignored |  | 1 | 2 | 3 | avg | Answer | 2
OR |  |  | Volts |  |  |  |  | Check | 20.3
2. KW from portable meter |  | 20.3 | Amps
OR | [5 empty] | Power Factor | 0.95
3. KW from volt-amp method (Use table at right) |  | Ignored |  |  |  | KW | 0
Answer - KW Calculation | 20.3
Input Horsepower | 6 | 27.2118 |  |  | Motor Load
Estimated thrust bearing losses (hp) | 6a | 0.2313 |  |  | Motor Eff. | 85% | C5
Estimated shaft losses (hp) | 6b | 0.09 |  |  | Nameplate HP | 20 | C3
Brake horsepower delivered to impeller (hp) | 7 | 22.8087 |  |  | Nplt Input HP | 23.5294
Impeller Efficiency (%) | 8 | 76.96% |  |  | Input HP | 27.2118
Overall Pumping Plant Efficiency (%) | 9 | 64.51% |  |  | Motor Load | 115.7%
KWH/AF | 10 | 78.7471
1 Pumping water level = Standing water level + Drawdown, 1a. Suction inches Hg = 1.133 ft of water
2 Discharge pressure at gauge (feet) = (Discharge pressure at gauge (psi) x 2.31 ) - Height of gauge above ground (ft)
3 Total lift = Pumping water level + Discharge pipe centerline above ground + Discharge pressure (all in feet)
OR (Horizontal Pumps) Total lift = Suction pressure (ft) - Suction pressure gauge height above ground (ft)
4 Total dynamic head (ft) =Total lift + Column friction losses + Discharge head loss
5 Water Horsepower = GPM x Total Dynamic Head/3960
6 Input HP =4.83 x (Kh for meter) x (M, usually = 1) x (Number of Meter Revolutions) / (Time for meter rev. in sec)
OR Input Horsepower =(KW from test meter) / 0.746
OR Input Horsepower =(KW from volt-amp method / 0.746)
6a Est. thrust bearing losses = Motor Eff*Input HP*1%
6b Est. shaft losses = 1HP per 100 feet of shaft (Shaft length in cell C13 is needed for this calc otherwise it is ignored)
7 Brake Horsepower delivered to impeller = (Input Horsepower * Motor Efficiency) - Est. thrust bearing losses - Est. shaft losses
(If no shaft length input in C10 shaft loss is ignored)
8 Impeller Efficiency (%) = Water Horsepower / Brakehorsepower x 100
9 Overall Pumping Plant Efficiency (%) = Water Horsepower/Input Horsepower x 100
10 KWH/AF = (IHP * .746)/ (GPM *60/325,850)

## Blank
ITRC Pump Efficiency Test Report | [7 empty] | Do not edit
2004-03-12
Nameplate HP on motor: |  |  | Flow Measurement Work Area |  |  |  |  | Collins or Prandtl Tube
Motor RPM |  |  | Choose Flow Rate Test Method |  |  |  |  | Hall Tube
Motor Efficiency |  |  | Pipe OD (inches) |  |  |  |  | Other type of flow meter
Meter factor (Kh): |  |  | Pipe wall thickness (inches) | [5 empty] | 3
Power Factor |  |  | Pipe ID (inches) |  |  | 0 |  | Check | 0
Depth of Pump |  |  | Find the box below that represents your flow test method. Look for "Complete"
Pump Make |  |  | Collins or Prandtl tube measurement |  |  |  | Ignore
Driver Make |  |  | If you have no data, leave or make blank do not enter 0
Discharge Head Type |  |  | Velocity Measurement (ft/s) - single transect
Column Diameter (in) |  |  | Left of CL
Shaft Length (ft) |  |  | Right of CL
Shaft Diameter (inches) |  |  | Avg. transect velocity (ft/s)
Vertical Pump TDH Data |  |  | Velocity Measurement (ft/sec) - second transect for Collins Tube
Standing Water Level below ground (ft) |  |  | Left of CL
Drawdown (ft) | 1 | Need PWL | Right of CL
Pumping Water Level (ft) |  |  | Average transect velocity (ft/s)
Column and screen Friction Losses (ft)
Discharge Head Loss (ft) |  |  | GPM Calculation
Avg. velocity in the pipe (ft/s)
Horizontal Pump TDH Data |  |  | Conversion for manometers |  |  | 0 | if applicable
Suction pressure (inches Hg) |  |  | Revised average velocity
Suction pressure (ft) | 1a | 0 | Pipe ID |  |  | 0
Suction pressure gauge height above ground (ft) |  |  | Multiplier |  |  | 0
|  |  | Calculated GPM |  |  | 0
Discharge pressure data for all pumps |  |  | OR
Discharge pipe centerline above ground (ft) |  |  | Hall tube measurement |  |  |  | Ignore
Height of gauge above ground (ft) |  |  | Avg. Velocity of a single transect (ft/s)
Discharge pressure at gauge (psi) |  |  | Avg. Velocity of second transect (ft/s)
Discharge pressure at gauge (ft) | 2 | 0 | Calculated GPM |  |  | 0
Total lift (ft) (commonly used by pump testers) | 3 | 0
Total dynamic head (ft) | 4 | 0 | OR
Flow rate (GPM) |  | Error |  |  |  |  | Complete
Water horsepower | 5 | #VALUE! | Other type of flow meter (GPM)
Water kW |  | #VALUE!
KW Calculation (Choose a method)
1. Number of dial rotations |  |  | Only needed if option 3 is chosen, otherwise ignore |  |  |  |  | 1.Dial Rotation | 1
Time for dial rotations (secs) |  |  | 3. Alternate volt-amp method for KW |  |  |  | Ignore | 2.Portable Meter | 2
Meter Constant |  |  | KW = V x A x PF x 1.732 / 1000 |  |  |  |  | 3.Volt-Amp Method | 3
Meter Factor, Kh |  |  | Do not input 0 - Leave blank for no data
KW from Meter |  | Error |  | 1 | 2 | 3 | avg | Answer | 2
OR |  |  | Volts |  |  |  |  | Check | 0
2. KW from portable meter |  |  | Amps
OR | [5 empty] | Power Factor | 0
3. KW from volt-amp method (Use table at right) |  | Ignored |  |  |  | KW | 0
Answer - KW Calculation | Error
Input Horsepower | 6 | Need KW |  |  | Motor Load
Estimated thrust bearing losses (hp) | 6a | Check Motor Eff. |  |  | Motor Eff. | 0% | C5
Estimated shaft losses (hp) | 6b | Need Shaft Length |  |  | Nameplate HP | 0 | C3
Brake horsepower delivered to impeller (hp) | 7 | #VALUE! |  |  | Nplt Input HP | Check Motor Eff.
Impeller Efficiency (%) | 8 | #VALUE! |  |  | Input HP | Need KW
Overall Pumping Plant Efficiency (%) | 9 | #VALUE! |  |  | Motor Load | #VALUE!
KWH/AF | 10 | #VALUE!
1 Pumping water level = Standing water level + Drawdown, 1a. Suction inches Hg = 1.133 ft of water
2 Discharge pressure at gauge (feet) = (Discharge pressure at gauge (psi) x 2.31 ) - Height of gauge above ground (ft)
3 Total lift = Pumping water level + Discharge pipe centerline above ground + Discharge pressure (all in feet)
OR (Horizontal Pumps) Total lift = Suction pressure (ft) - Suction pressure gauge height above ground (ft)
4 Total dynamic head (ft) =Total lift + Column friction losses + Discharge head loss
5 Water Horsepower = GPM x Total Dynamic Head/3960
6 Input HP =4.83 x (Kh for meter) x (M, usually = 1) x (Number of Meter Revolutions) / (Time for meter rev. in sec)
OR Input Horsepower =(KW from test meter) / 0.746
OR Input Horsepower =(KW from volt-amp method / 0.746)
6a Est. thrust bearing losses = Motor Eff*Input HP*1%
6b Est. shaft losses = 1HP per 100 feet of shaft (Shaft length in cell C13 is needed for this calc otherwise it is ignored)
7 Brake Horsepower delivered to impeller = (Input Horsepower * Motor Efficiency) - Est. thrust bearing losses - Est. shaft losses
(If no shaft length input in C10 shaft loss is ignored)
8 Impeller Efficiency (%) = Water Horsepower / Brakehorsepower x 100
9 Overall Pumping Plant Efficiency (%) = Water Horsepower/Input Horsepower x 100
10 KWH/AF = (IHP * .746)/ (GPM *60/325,850)